INDIAN INSTITUTE OF ENGINEERING SCIENCE AND TECHNOLOGY                                                      SHIBPUR, P.O. Botanic Garden (Formerly Bengal Engineering And Science University)

HOWRAH (West Bengal, India)-711103

Phone: 033 26681503, 033 26684561	Fax: 033 26682916

Tender No:-05/DY.REG./19-20 							           Date:-24.05.2019

Notice Inviting  Tender

Sealed quotations are invited from bonafide Electrical Contractor, having valid electrical license for building electrification works for Renovation of Electrical wiring in PHD Scholar's room of   Computer Science Department at 2nd floor of Main Building and Power Feeding arrangement for Roll Crusher machine in Mineral Dressing Lab of Mining Engineering Department at ground floor  of Main Building in the Campus of  IIEST, Shibpur, Howrah-711103. The quotation will be received in the drop box at the Office of  the Registrar, Purchase section between 11.00 a.m and 5.00 p.m on all working days latest by 03.06.2019. Opening on 04.06.2019 at 1.30 p.m.at the Office of the university Engineer.

REGISTRAR

Terms & Conditions:-

- To qualify for award of the contract the bidder should have valid electrical license for building electrification works  and should have satisfactory completed at least one similar work of value not less than Rs 80,000.00

- Quotation are to be submitted as per above mentioned format.

- All rates quoted should be inclusive of all taxes, levies & duties and Labor Welfare Cess, The rates should be   quoted    both in figures and words. Request for inclusion of any tax/levy at later stage will not be entertained.

- Transportation, Packing, Forwarding and Insurance Charges if any to be charged should be   specifically indicated.

- The Institute reserves the right to accept or reject all or any of the tenders without assigning any reason whatsoever. The decision of the Institute shall be final in case of any dispute.

- The work should be completed within 15 days of issuing of order.

- Materials & accessories supplied/used should be as per specification and of Approved Quality (B.I.S.) or by the authorised    officer of I.I.E.S.T,Shibpur.

- The work should be completed within stipulated period as indicated in the work-order.  A  Liquidated damages @ 0.5% per week, subject to maximum of 2% of the value of work-order, beyond which the Employer may cancel the Contract.

- Bills in Triplicate should be presented for payment within 15days of supply/completion of work.

- The Order no. is to be noted on both challan & Bill.

- All bills are to be accompanied by order copies and challans as received.

- Payment will be made within 60 days of Submission of proper bills, challans etc. by A/c payee cheque, no Cash payment will be made under any circumstances.

- Last date of submission of quotation is 03.06.2019  upto 5.00 p.m at the Office of the Registrar, Purchase section.

- Opening on 04.06.2019 at 1.30 pm at the office of the University Engineer.

Deputy Registrar

(Store and Purchase)

Copy To: 1.To be displayed on the Institute Website

2. All Notice Board

3. Office of the University Engineer

Indian Institute of Engineering Science and Technology, Shibpur

Howrah-711 103

Name of Tender: Renovation  of  Electrical wiring  in PHD Scholar's room of   Computer Science Department at 2nd floor of Main Building  and  Power Feeding arrangement for Roll Crusher machine in Mineral Dressing Lab of Mining Engineering Department at ground floor  of Main Building  in the Campus of  IIEST, Shibpur, Howrah-711103.

1.	Name of the Firm		:

(in block letter)

2.	Office Address		:

3.        Phone No.	                         :

- Whether Partnership / Proprietorship Firm  :

5.	Name of Partner(s) / Proprietor(s):
6.	PAN  No.	                                :

- Trade Licence No.                          :

- Electrical Licence                           :

- GST  No.	                     :

10.	Quoted rate:

(Use separate sheet, if required)

| Bill of quantities for the work of: Renovation of Electrical wiring in PHD Scholar's room of Computer Science Department at 2nd floor of Main Building and Power Feeding arrangement for Roll Crusher machine in Mineral Dressing Lab of Mining Engineering Department at ground floor of Main Building in the Campus of IIEST, Shibpur, Howrah-711103. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| S.L. No. | Description of work | Unit | Qty. | Unit Rate (In Rs) | Amount (In Rs) |
| 1 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) partly in 20mm size PVC rigid conduit 'FR' (Precision make) [for ceiling portion only] and in 19mm bore, 3mm thick polythene pipe [for horizontal & vertical run embedded in wall], with 1x22/0.3 (1.5 sqmm)single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, to light/fan/call bell points with Piano Key type switch fixed on MS CRC sheet metal (16 SWG) switch board on wall complete with 2 no. “Ph & N” copper bar incl. bakelite/ Perspex top cover 3 mm thick and incl. 175x100x65mm inspection box, making earthing attachment, painting the MS box and mending good the damages to original finish [only PVC Rigid Conduit on ceiling and remaining portion concealed] (Average Run- 9 mtr) | point | 14 |  |  |
| 2 | On Board Plug. | point | 2 |  |  |
| 3 | Supply and fixing of 4 way MCB SS enclosure with IP-20/30 protection, S&F of 415 V,32 A FP,MCB incl necessary connection as to G.S.(Legrand) | Set. | 1 |  |  |
| 4 | Supplying and fixing 4-way double door Horizontal TPN MCB Distribution board with IP-42/43 protection, concealed in wall after cutting the wall & mending good the damages to original finish incl. Inter connection with suitable size of copper wire and neutral link & provision for earthing attachment. a) Incommer 63 Amps TP MCB-01Nos, b) Out going 6-32 Anps SP MCB-12 Nos. | Set. | 1 |  |  |
| 5 | Supplying and fixing of (2+12) way, double-door SPN MCB Distribution Board with IP-42/43 protection, concealed in wall after cutting the wall & mending good the damages to original finish incl. Inter connection with suitable size of copper wire and neutral link & provision for earthing attachment. a) Incommer 40 Amps DP MCB-01Nos, b) Out going 6-32 Anps SP MCB-12 Nos. | Set. | 1 |  |  |
| 6 | Supply & Fixing 240 V, 25A Modular type socket, 25 A, Modular type starter (Brand approved by EIC) with 25A Modular switch type DP MCB (C-Curve) and 6 Module GI Modular type switch board with 6 Module top cover plate flushed in wall incl. S&F switch board and cover plate and making necy. connections with PVC Cu wire and earth continuity wire etc. | Set. | 2 |  |  |
| 7 | Distribution wiring in 1.1 KV single core stranded 'FR'PVC insulated & unsheathed copper wire of 2 x 56/0.3 (4 sqmm) + 1 x 36/0.3 (2.5 sqmm) ECC (Brand approved by EIC) in 20mm size PVC rigid conduit 'FR' (Precision make) incl. necy. fittings as required. | RM | 60 |  |  |
| 8 | Distribution wiring in 1.1 KV single core stranded 'FR'PVC insulated & unsheathed copper wire of 2 x 36/0.3 (2.5 sqmm) + 1 x 22/0.3 (1.5 sqmm) ECC (Brand approved by EIC) in 20mm size PVC rigid conduit 'FR' (Precision make) incl. necy. fittings as required. | RM | 180 |  |  |
| 9 | Supply & Fixing 240 V, 20A, plug socket with separate 20 A Piano key type switch (Brand approved by EIC) on sheet metal switch board embedded in wall incl. S & F 150x100x65mm MS (16SWG) switch board and bakelite/perspex top cover of 3mm thick by Brass screws after making housing for switch by cutting bakelite/perspex cover and making necessary connections as required | Each. | 2 |  |  |
| 10 | Supply & Fixing 240 V, 20A, plug socket with separate 20 A Piano key type switch (Brand approved by EIC) on sheet metal switch board embedded in wall incl. S & F 150x100x65mm MS (16SWG) switch board and bakelite/perspex top cover of 3mm thick by Brass screws after making housing for switch by cutting bakelite/perspex cover and making necessary connections as required | Each. | 6 |  |  |
| 11 | Supply & Fixing Socket type fan regulator (Step type) (Brand approved by EIC) on existing sheet metal switch board with bakelite/perspex top cover by screw after making housing for regulator knob by cutting bakelite/perspex top cover incl. making necy. connections etc. | Each. | 2 |  |  |
| 12 | S&F of twin LED lighting fittings (cat No- TMC 501 P/ 2X T-LED 22 make Philips) with 2 x T-LED 20 W lamp (1200mm T-8 LED Tube retrofitted Aluminium body 20 Wayy (Make CG ) with L-Clamp down rod as to GS. | Set. | 6 |  |  |
| 13 | Extra for suspension exceeding 25 cm with S&F additional 2 no. 20 mm dia EI conduit (14 SWG) supports & necy. PVC insulated wire and painting etc. as required by 2x24/0.20 mm (1.5sqmm.) flexible copper wire of 1.10 mt. length. | RM | 6 |  |  |
| 14 | S& F A.C Ceiling Fan 1400 mm sweep complete with blade, canopy, frock,rubber bush etc as reqd. (Make Orient P.S.P.O Summer cool) | Nos. | 2 |  |  |
| 15 | Supply & Fixing 240 V, 3 nos. 20A plug socket with separate 3 nos. 20A Piano key type switch, indicator & 16A kit-kat flush type fuse (Brand approved by EIC) on sheet metal switch board embedded in wall incl. S & F 300x200x65mm MS (16SWG) switch board and bakelite/perspex top cover of 3mm thick by Brass screws after making housing for switch by cutting bakelite/perspex cover and making necessary connections as required. | Each | 1 |  |  |
| 16 | Supply & Fixing 240 V, 20A, plug socket with separate 20 A Piano key type switch (Brand approved by EIC) on sheet metal switch board embedded in wall incl. S & F 150x100x65mm MS (16SWG) switch board and bakelite/perspex top cover of 3mm thick by Brass screws after making housing for switch by cutting bakelite/perspex cover and making necessary connections as required | Each | 2 |  |  |
| 17 | Supplying & Fixing Industrial Plug & Socket board with 415 V, 30A, TPN & Earth Metal Industrial Plug socket & 30A Industrial top incl. S&F 32 A TPN/FP MCB breaking capcity 10kA (C- Curve) in SS enclosure fixed on wall and cecessary conection. | Each | 1 |  |  |
| S.L. No. | Description of work | Unit | Qty. | Unit Rate (In Rs) | Amount (In Rs) |
| 18 | Supply and laying of 1.1. KV grade XLPE cable 4 core 25 sqmm on wall/surface incl. S & F MS saddles with earthing attachment in 2 x 10 SWG GI (Hot Dip) Wire, making holes etc. as necy., mending good damages and painting | RM | 40 |  |  |
| 19 | Supply and laying of 1.1. KV grade XLPE cable 4 core 10 sqmm on wall/surface incl. S & F MS saddles with earthing attachment in 2 x 10 SWG GI (Hot Dip) Wire, making holes etc. as necy., mending good damages and painting | RM | 45 |  |  |
| 20 | Supplying and fixing compression type gland complete with brass gland, brass ring & rubber ring for dust & moisture-proof entry of XLPE/PVC armoured cables of 4 core 10 sqmm. | Each | 4 |  |  |
| 21 | Finishing the end of 4 core 10 sqmm. XLPE/PVC armoured cables by crimping method incl. supplying and fixing solderless socket (Dowels make), tapes, anticorrosive paste & jointing materials | Set. | 4 |  |  |
| 22 | Supplying and fixing compression type gland complete with brass gland, brass ring & rubber ring for dust & moisture-proof entry of XLPE/PVC armoured cables of 4 core 25sqmm. | Each | 2 |  |  |
| 23 | Finishing the end of 4 core 25sqmm. XLPE/PVC armoured cables by crimping method incl. supplying and fixing solderless socket (Dowels make), tapes, anticorrosive paste & jointing materials | Set. | 2 |  |  |
| 24 | Finishing of the PVC insulated wire ends by socketting with pin/ ring type copper sockets and insulated tapes etc., including supplying sockets, tapes. |  |  |  |  |
| 24 (a) | 2.5sqmm cu wire. | Nos. | 30 |  |  |
| 24(b) | 4 sqmm cu wire. | Nos. | 8 |  |  |
| 25 | Dismantling the existing wiring as required. | lot. | 1 |  |  |
| TOTAL (In Rs) |  |  |  |  |  |

To

Deputy Registrar

Store and Purchase

IIEST’S, Howrah-711103

I/WE agree to execute the work in accordance to requirement at the above quoted items rates for a total price of Rs----------------------------     (Rupees                                                                                                                                  )

Authorized Signature:------------------------------               Dated:-                        Address:-

Name & Title of Signatory:

Name of the bidder and Seal:

Notes: 1) Quantities mentioned in the B.O.Q are as per estimate. Actual quantities may vary according to the requirement at site; payment will be made on pro-rata basis on actual executed quantity.

2) The bidder is advised to visit the site of work at his own expense and obtain all information that may be necessary for preparing the quotation. The Bidder  enclosed attested copy of Trade License/GST No/Pan Card/ P Tax certificate and completion certificate of similar work and other document etc with the application.